## How to calculate
How to calculate the Address ?
| Example: | When you use J60
|  | J | 60
|  | ↓ | ↓
|  | 13 | 60
The holding register address is:
| 400001 | + | 13 | x | 256 | + | 60 | = | 403389
Since FC6A's holding registers start from 400001, the Modbus table below are calculated based on FC6A (400001).
Depending on the specification of the host controller, the start address of the holding register area may be 400000. In that cases, please replace 400001 in the above formula with 400000.
Wiring for Modbus RTU (RS-485) *Connecting on Modular Jack.
| FC6A All-in-One |  |  |  | VF1A Doesa
| No. | Signal name | Cable colour |  | No. | Signal name | Cable colour
| 1 | - | White/ Orange |  | 1 | Reserve | -
| 2 | - | Orange |  | 2 | GND | -
| 3 | - | White/ Green |  | 3 | Reserve | -
| 4 | A+ | Blue |  | 4 | DX- | -
| 5 | B- | White/ Blue |  | 5 | DX＋ | -
| 6 | - | Green |  | 6 | NC | -
| 7 | - | White/ Brown |  | 7 | GND | -
| 8 | SG | Brown |  | 8 | NC | -
Wiring for Modbus RTU (RS-485) *Connecting on Terminal block.
| FC6A All-in-One |  |  |  | VF1A Doesa
| No. | Signal name | Cable colour |  | No. | Signal name | Cable colour
| 1 | - | White/ Orange |  | - | - | -
| 2 | - | Orange |  | - | - | -
| 3 | - | White/ Green |  | - | - | -
| 4 | A+ | Blue |  | 4 | DX- | -
| 5 | B- | White/ Blue |  | 5 | DX＋ | -
| 6 | - | Green |  | - | - | -
| 7 | - | White/ Brown |  | - | - | -
| 8 | SG | Brown |  | - | - | -
Wiring for Modbus RTU (RS-485) *Connecting on Expansion card(VF1A-RS485)

## F
FUNCTION CODE | Detail | Address
F00 | Data Protection | 400001
F01 | Frequency command 1 | 400002
F02 | Operation method | 400003
F03 | Maximum frequency 1 | 400004
F04 | Base frequency 1 | 400005
F05 | Rated voltage at base frequency 1 | 400006
F06 | Maximum output voltage 1 | 400007
F07 | Acceleration time 1 | 400008
F08 | Deceleration time 1 | 400009
F09 | Torque boost 1 | 400010
F10 | Electronic thermal overload protection for motor 1 (Select motor characteristics) | 400011
F11 | Electronic thermal overload protection for motor 1 (Overload detection level) | 400012
F12 | Electronic thermal overload protection for motor 1 (Thermal time constant) | 400013
F14 | Restart mode after momentary power failure (Mode selection) | 400015
F15 | Frequency Limiter (High) | 400016
F16 | Frequency Limiter (Low) | 400017
F18 | Bias (Frequency command 1) | 400019
F20 | DC Braking 1 (Braking starting frequency) | 400021
F21 | DC Braking 1 (Braking level) | 400022
F22 | DC Braking 1 (Braking time) | 400023
F23 | Starting frequency 1 | 400024
F24 | Starting frequency 1 (Holding time) | 400025
F25 | Stopping frequency | 400026
F26 | Motor sound (Carrier frequency) | 400027
F27 | Motor sound (Tone) | 400028
F29 | Terminal [FM] (Function selection) | 400030
F30 | Terminal [FM] (Gain to output voltage) | 400031
F31 | Terminal [FM] (Function Selection) | 400032
F33 | Terminal [FM] (Pulse Rate) | 400034
F37 | Load Selection/Auto Torque Boost/Auto Energy Saving Operation | 400038
F38 | Stop Frequency (Detection System) | 400039
F39 | Stop Frequency (Holding Time) | 400040
F40 | Torque limiting 1 (Driving) | 400041
F41 | Torque limiting 1 (Braking) | 400042
F42 | Control Mode Selection | 400043
F43 | Current Limiter (Mode selection) | 400044
F44 | Current Limiter (Level) | 400045
F50 | Electronic Thermal Overload Protection for Braking Resistor (Discharging capability) | 400051
F51 | (Allowable average loss) | 400052
F52 | (for braking resistor) | 400053
F80 | HHD/HND/HD/ND switching | 400081

## E
FUNCTION CODE | Detail | Address
E01 | Terminal [X1] (Function Selection) | 400258
E02 | Terminal [X2] (Function Selection) | 400259
E03 | Terminal [X3] (Function Selection) | 400260
E04 | Terminal [X4] (Function Selection) | 400261
E05 | Terminal [X5] (Function Selection) | 400262
E10 | Acceleration time 2 | 400267
E11 | Deceleration time 2 | 400268
E12 | Acceleration time 3 | 400269
E13 | Deceleration time 3 | 400270
E14 | Acceleration time 4 | 400271
E15 | Deceleration time 4 | 400272
E16 | Torque limiting 2 (Driving) | 400273
E17 | Torque limiting 2 (Braking) | 400274
E20 | Terminal [Y1] (Function Selection) | 400277
E21 | Terminal [Y2] | 400278
E27 | Terminal [30A/B/C] | 400284
E29 | Frequency level detection delay timer | 400286
E30 | Frequency Arrival (Hysteresis width) | 400287
E31 | Frequency Detection (FDT) (Detection level) | 400288
E32 | Frequency Detection (FDT) (hysteresis width) | 400289
E34 | Overload early warning/Current detection (level) | 400291
E35 | Overload early warning/Current detection (timer) | 400292
E36 | Frequency Detection 2 (FDT 2) (Detection Level) | 400293
E37 | Current detection 2/Low current detection (Detection Level) | 400294
E38 | Current detection 2/Low current detection (timer) | 400295
E39 | Coefficient for Constant Feeding Rate Time | 400296
E42 | LED Display filter | 400299
E43 | LED Monitor (Item selection) | 400300
E44 | LED Monitor (Display when stopped) | 400301
E48 | LED Monitor details (Speed monitor item) | 400305
E49 | Torque command monitor (Polarity selection) | 400306
E50 | Coefficient for Speed Indication | 400307
E51 | Display Coefficient for Input Watt-hour Data | 400308
E52 | Keypad (Menu display mode) | 400309
E54 | Frequency detection 3 (Operation level) | 400311
E55 | Current detection 3 (Operation level) | 400312
E56 | Current detection 3 (Timer time) | 400313
E59 | Switch function of C1 terminal | 400316
E61 | Terminal [12] (Extended function selection) | 400318
E62 | Terminal [C1] (C1 function) (Extended function selection) | 400319
E63 | Terminal [C1] (V2 function) (Extended function selection) | 400320
E64 | Saving Digital Reference Frequency | 400321
E65 | Reference Loss Detection | 400322
E76 | DC link bus low-voltage detection level | 400333
E78 | Torque detection 1 (Operation level) | 400335
E79 | Torque detection 1 (Timer time) | 400336
E80 | Detect Torque 2/Detect Low Torque 2 (Detection level) | 400337
E81 | Detect Torque 2/Detect Low Torque 2 (Timer) | 400338
E98 | Terminal [FWD] (Function selection) | 400355
E99 | Terminal [REV] | 400356

## C
FUNCTION CODE | Detail | Address
C01 | Jump Frequency 1 | 400514
C02 | Jump Frequency 2 | 400515
C03 | Jump Frequency 3 | 400516
C04 | Jump Frequency Width | 400517
C05 | Multi-Frequency 1 | 400518
C06 | Multi-Frequency 2 | 400519
C07 | Multi-Frequency 3 | 400520
C08 | Multi-Frequency 4 | 400521
C09 | Multi-Frequency 5 | 400522
C10 | Multi-Frequency 6 | 400523
C11 | Multi-Frequency 7 | 400524
C12 | Multi-Frequency 8 | 400525
C13 | Multi-Frequency 9 | 400526
C14 | Multi-Frequency 10 | 400527
C15 | Multi-Frequency 11 | 400528
C16 | Multi-Frequency 12 | 400529
C17 | Multi-Frequency 13 | 400530
C18 | Multi-Frequency 14 | 400531
C19 | Multi-Frequency 15 | 400532
C20 | Jogging Frequency | 400533
C21 | Pattern operation/timer operation (Mode selection) | 400534
C22 | Pattern operation (Stage 1) | 400535
C23 | Pattern operation (Stage 2) | 400536
C24 | Pattern operation (Stage 3) | 400537
C25 | Pattern operation (Stage 4) | 400538
C26 | Pattern operation (Stage 5) | 400539
C27 | Pattern operation (Stage 6) | 400540
C28 | Pattern operation (Stage 7) | 400541
C30 | Frequency command 2 | 400543
C31 | Analog Input Adjustment for [12] (offset) | 400544
C32 | Analog Input Adjustment for [12] (Gain) | 400545
C33 | Analog Input Adjustment for [12] (Filter time constant) | 400546
C34 | Analog Input Adjustment for [12] (Gain base point) | 400547
C35 | Analog Input Adjustment for [12] (Polarity) | 400548
C36 | Analog Input Adjustment for [C1] (C1 function) (Offset) | 400549
C37 | Analog Input Adjustment for [C1] (C1 function) (Gain) | 400550
C38 | Analog Input Adjustment for [C1] (C1 function) (Filter time constant) | 400551
C39 | Analog Input Adjustment for [C1] (C1 function) (Gain base point) | 400552
C40 | Terminal [C1] (C1 function) (Range selection) | 400553
C41 | Analog Input Adjustment for [C1]) (V2 function) (Offset) | 400554
C42 | Analog Input Adjustment for [C1] (V2 function) (Gain) | 400555
C43 | Analog Input Adjustment for [C1] (V2 function) (Filter time constant) | 400556
C44 | Analog Input Adjustment for [C1] (V2 function) (Gain base point) | 400557
C45 | Analog input Adjustment for [V2] (Polarity) | 400558
C50 | Bias (Frequency command 1) (Bias base point) | 400563
C53 | Selection of Normal/Inverse Operation (Frequency command 1) | 400566
C55 | Analog input adjustment (Terminal [12]) (Bias) | 400568
C56 | Analog input adjustment (Terminal [12]) (Bias reference point) | 400569
C58 | Analog input adjustment (Terminal [12]) (Display unit) | 400571
C59 | Analog input adjustment (Terminal [12]) (Maximum scale) | 400572
C60 | Analog input adjustment (Terminal [12]) (Minimum scale) | 400573
C61 | Analog input adjustment (Terminal [C1] (C1 function)) (Bias) | 400574
C62 | Analog input adjustment (Terminal [C1] (C1 function))(Bias reference point) | 400575
C64 | Analog input adjustment (Terminal [C1] (C1 function))(Display unit) | 400577
C65 | Analog input adjustment (Terminal [C1] (C1 function))(Maximum scale) | 400578
C66 | Analog input adjustment (Terminal [C1] (C1 function))(Minimum scale) | 400579
C67 | Analog input adjustment (Terminal [C1] (V2 function)) (Bias) | 400580
C68 | Analog input adjustment (Terminal [C1] (V2 function))(Bias reference point) | 400581
C70 | Analog input adjustment (Terminal [C1] (V2 function))(Display unit) | 400583
C71 | Analog input adjustment (Terminal [C1] (V2 function))(Maximum scale) | 400584
C72 | Analog input adjustment (Terminal [C1] (V2 function))(Minimum scale) | 400585
C89 | Frequency correction with communication function 1 (Numerator) | 400602
C90 | Frequency correction with communication function 2 (Denominator) | 400603

## P
FUNCTION CODE | Detail | Address
P01 | Motor 1 (No. of poles) | 400770
P02 | Motor 1 (Rated Capacity) | 400771
P03 | Motor 1 (Rated current) | 400772
P04 | Motor 1 (Auto-tuning) | 400773
P05 | Motor 1 (Online Tuning) | 400774
P06 | Motor 1 (No-load current) | 400775
P07 | Motor 1 (%R1) | 400776
P08 | Motor 1 (%X) | 400777
P09 | Motor 1 (Slip compensation gain for driving) | 400778
P10 | Motor 1 (Slip compensation response time) | 400779
P11 | Motor 1 (Slip compensation gain (Braking)) | 400780
P12 | Motor 1 (Rated slip frequency) | 400781
P13 | Motor 1 (Iron loss coefficient 1) | 400782
P16 | Motor 1 (Magnetic saturation coefficient 1) | 400785
P17 | Motor 1 (Magnetic saturation coefficient 2) | 400786
P18 | Motor 1 (Magnetic saturation coefficient 3) | 400787
P19 | Motor 1 (Magnetic saturation coefficient 4) | 400788
P20 | Motor 1 (Magnetic saturation coefficient 5) | 400789
P30 | Motor 1 (PMSM drive magnetic pole position detection mode) | 400799
P53 | Motor 1 (%X compensation coefficient 1) | 400822
P55 | Motor 1 (Vector control torque current) | 400824
P56 | Motor 1 (Vector control t inductitive voltage coefficient) | 400825
P60 | Motor 1 (PMSM armature resistance) | 400829
P61 | Motor 1 (PMSM d-axis inductance) | 400830
P62 | Motor 1 (PMSM q-axis inductance) | 400831
P63 | Motor 1 (PMSM induced voltage) | 400832
P64 | Motor 1 (PMSM iron loss) | 400833
P65 | Motor 1 (PMSM d-axis inductance magnetic saturation correction) | 400834
P74 | Motor 1 (PMSM reference current at starting) | 400843
P83 | Motor 1 (PMSM, for manufacturer) | 400852
P84 | Motor 1 (PMSM, for manufacturer) | 400853
P85 | Motor 1 (PMSM flux limiting value) | 400854
P86 | Motor 1 (PMSM, for manufacturer) | 400855
P87 | Motor 1 (PMSM reference current for polarity discrimination) | 400856
P88 | Motor 1 (PMSM, for manufacturer) | 400857
P89 | Motor 1 (PMSM, for manufacturer) | 400858
P90 | Motor 1 (PMSM overcurrent protection level) | 400859
P99 | Motor 1 Selection | 400868

## H
FUNCTION CODE | Detail | Address
H02 | Data initialization (Initial value selection) | 401027
H03 | Data Initialization | 401028
H04 | Auto-reset (times) | 401029
H05 | Auto-reset (Reset interval) | 401030
H06 | Cooling Fan ON/OFF Control | 401031
H07 | Acceleration/Deceleration Pattern | 401032
H08 | Rotation Direction Limitation | 401033
H09 | Start Mode (Auto search) | 401034
H11 | Deceleration Mode | 401036
H12 | Instantaneous Overcurrent Limiting (Mode selection) | 401037
H13 | Restart Mode after Momentary Power Failure (Restart time) | 401038
H14 | Restart Mode after Momentary Power Failure (Frequency fall rate) | 401039
H15 | Restart Mode after Momentary Power Failure (Holding DC voltage) | 401040
H16 | (Allowable momentary power failure time) | 401041
H18 | Torque control (Mode selection) | 401043
H26 | Thermistor (Mode selection) | 401051
H27 | Thermistor (Level) | 401052
H28 | Droop control | 401053
H30 | Communications Link Function (Mode selection) | 401055
H42 | Capacitance of DC Link Bus Capacitor | 401067
H43 | Cumulative Run Time of Cooling Fan | 401068
H44 | Startup Times 1 of Motor | 401069
H45 | Mock Alarm | 401070
H46 | Restart Mode after Momentary Power Failure (Restart time) | 401071
H47 | Initial Capacitance of DC Link Bus Capacitor | 401072
H48 | Cumulative Run Time of Capacitors on the PCB | 401073
H49 | Starting Mode (Delay time) | 401074
H50 | Non-linear V/f Pattern 1 (Frequency) | 401075
H51 | Non-linear V/f Pattern 1 (Voltage) | 401076
H52 | Non-linear V/f 2 (Frequency) | 401077
H53 | Non-linear V/f 2 (Voltage) | 401078
H54 | Acceleration time (Jogging) | 401079
H55 | Deceleration time (Jogging operation) | 401080
H56 | Deceleration Time for Forced Stop | 401081
H57 | 1st S-curve range at acceleration (start) | 401082
H58 | 2nd S-curve range at deceleration (end) | 401083
H59 | 1st S-curve range at acceleration (start) | 401084
H60 | 2nd S-curve range at deceleration (end) | 401085
H61 | UP/DOWN Control Initial frequency setting | 401086
H63 | Low Limiter (Mode selection) | 401088
H64 | Low Limiter (Lower limiting frequency) | 401089
H65 | Non-linear V/f 3 (Frequency) | 401090
H66 | Non-linear V/f 3 (Voltage) | 401091
H68 | Slip Compensation 1 (Operating conditions) | 401093
H69 | Automatic deceleration (Mode selection) | 401094
H70 | Overload prevention control | 401095
H71 | Deceleration Characteristics | 401096
H72 | Main Power Down Detection (Mode Selection) | 401097
H74 | Torque limiting (Control target) | 401099
H76 | Torque Limiter (Frequency increment limit for braking) | 401101
H77 | Main circuit capacity life (remaining hour) | 401102
H78 | Maintenance setting time (M1) | 401103
H79 | No. of maintenance setting starting times (M1) | 401104
H80 | Output Current Fluctuation Damping Gain for Motor 1 | 401105
H81 | Light alarm selection 1 | 401106
H82 | Light alarm selection 2 | 401107
H84 | Pre-excitation (initial level) | 401109
H85 | Pre-excitation (time) | 401110
H89 | Pre-excitation (For manufacturer) | 401114
H91 | PID feedback disconnection detection | 401116
H92 | Continue to Run (P-component: gain) | 401117
H93 | Continue to Run (I-component: time) | 401118
H94 | Cumulative Motor Run Time 1 | 401119
H95 | DC braking (Braking response mode) | 401120
H96 | STOP key priority / Start check function | 401121
H97 | Clear alarm data | 401122
H98 | Protection/Maintenance Function (Mode selection) | 401123
H101 | Destination setting | 401126
H111 | UPS operation level | 401136
H114 | Anti-regenerative control (Operation level) | 401139
H147 | Speed control (Jogging) (Feed forward gain) | 401172
H154 | Torque bias (Function selection) | 401179
H155 | Torque bias (Setting level 1) | 401180
H156 | Torque bias (Setting level 2) | 401181
H157 | Torque bias (Setting level 3) | 401182
H158 | Torque bias (Mechanical loss compensation) | 401183
H159 | Torque bias (Startup timer) | 401184
H161 | Torque bias (Shutdown timer) | 401186
H162 | Torque bias (Limiter) | 401187
H173 | Magnetic flux level at light load | 401198
H180 | Brake signal (Check time for brake operation) | 401205
H193 | User initial value (Save) | 401218
H194 | User initial value (Protection) | 401219
H195 | DC braking (Braking time at startup) | 401220
H196 | For manufacturer | 401221
H197 | User password 1 (Protection mode selection) | 401222
H198 | User password 1 (Setting/comparison) | 401223
H199 | User password (Protection enabled) | 401224

## A
FUNCTION CODE | Detail | Address
A01 | Maximum frequency 2 | 401282
A02 | Base frequency 2 | 401283
A03 | Rated voltage at base frequency 2 | 401284
A04 | Maximum output voltage 2 | 401285
A05 | Torque boost 2 | 401286
A06 | Electronic thermal overload protection for motor 2 (Select motor characteristics) | 401287
A07 | Electronic thermal overload protection for motor 2 (Overload detection level) | 401288
A08 | Electronic thermal overload protection for motor 2 (Thermal time constant) | 401289
A09 | DC Braking 2 (Braking starting frequency) | 401290
A10 | DC Braking 2 (Braking level) | 401291
A11 | DC Braking 2 (Braking time) | 401292
A12 | Starting frequency 2 | 401293
A13 | Load Selection/Auto Torque Boost/Auto Energy Saving Operation 2 | 401294
A14 | Control Mode Selection 2 | 401295
A15 | Motor 2 (No. of poles) | 401296
A16 | Motor 2 (Rated Capacity) | 401297
A17 | Motor 2 (Rated current) | 401298
A18 | Motor 2 (Auto-tuning) | 401299
A19 | Motor 2 (Online-tuning) | 401300
A20 | Motor 2 (No-load current) | 401301
A21 | Motor 2 (%R1) | 401302
A22 | Motor 2 (%X) | 401303
A23 | Motor 2 (Slip compensation gain for driving) | 401304
A24 | Motor 2 (Slip compensation response time) | 401305
A25 | Motor 2 (Slip compensation gain for braking) | 401306
A26 | Motor 2 (Rated slip frequency) | 401307
A27 | Motor 2 (Iron loss coefficient 1) | 401308
A30 | Motor 2 (Magnetic saturation coefficient 1) | 401311
A31 | Motor 2 (Magnetic saturation coefficient 2) | 401312
A32 | Motor 2 (Magnetic saturation coefficient 3) | 401313
A33 | Motor 2 (Magnetic saturation coefficient 4) | 401314
A34 | Motor 2 (Magnetic saturation coefficient 5) | 401315
A39 | Motor 2 Selection | 401320
A40 | Slip Compensation 2 (Operating conditions) | 401321
A41 | Output Current Fluctuation Damping Gain 2 | 401322
A43 | Speed control 2 (Speed command filter) | 401324
A44 | Speed control 2 (Speed detection filter) | 401325
A45 | Speed control 2 P (Gain) | 401326
A46 | Speed control 2 I (Integration time) | 401327
A47 | Speed control 2 I (FF gain) | 401328
A49 | Speed control 2 I (Notch filter resonance frequency) | 401330
A50 | Speed control 2 I (Notch filter attenuation level) | 401331
A51 | Cumulative Motor Run Time 2 | 401332
A52 | Startup Times of Motor 2 | 401333
A53 | Motor 2 (%X compensation efficient 1) | 401334
A55 | Motor 2 (Vector control torque current) | 401336
A56 | Motor 2 (Vector control inductive voltage coefficient) | 401337
A98 | Motor 2 (Function selection) | 401379

## b
FUNCTION CODE | Detail | Address
b43 | Speed control 3 (Speed command filter) | 404652
b44 | Speed control 3 (Speed detection filter) | 404653
b45 | Speed control 3 P (Gain) | 404654
b46 | Speed control 3 I (Integration time) | 404655
b47 | Speed control 3 FF (Gain) | 404656
b49 | Speed control 3 (Notch filter resonance frequency) | 404658
b50 | Speed control 3 (Notch filter attenuation level) | 404659

## r
FUNCTION CODE | Detail | Address
r43 | Speed control 4 (Speed command filter) | 402604
r44 | Speed control 4 (Speed detection filter) | 402605
r45 | Speed control 4 P (Gain) | 402606
r46 | Speed control 4 I (Integration time) | 402607
r47 | Speed control 4 FF (Gain) | 402608
r49 | Speed control 4 (Notch filter resonance frequency) | 402610
r50 | Speed control 4 (Notch filter attenuation level) | 402611

## J
FUNCTION CODE | Detail | Address
J01 | PID control (Mode selection) | 403330
J02 | PID control (Remote command) | 403331
J03 | PID control P (gain) | 403332
J04 | PID control I (Integration time) | 403333
J05 | PID control D (Derivative time) | 403334
J06 | PID control (Feedback filter) | 403335
J10 | PID control (Anti reset windup) | 403339
J11 | PID control (Select alarm output) | 403340
J12 | PID control (Upper level alarm (AH)) | 403341
J13 | PID control (Lower level alarm (AL)) | 403342
J15 | PID control (Stop frequency for slow flowrate) | 403344
J16 | PID control (Slow flowrate level stop latency) | 403345
J17 | PID control (Starting frequency) | 403346
J18 | PID control (Upper limit of PID process output) | 403347
J19 | PID control (Lower limit of PID process output) | 403348
J23 | PID control (Startup feedback deviation following low liquid level stop) | 403352
J24 | PID control (Startup delay time following low liquid level stop) | 403353
J57 | PID control (Dancer reference position) | 403386
J58 | PID control (Detection width of Dancer position deviation ) | 403387
J59 | PID control P (gain) 2 | 403388
J60 | PID control I (Integral time) 2 | 403389
J61 | PID control D (Derivative time) 2 | 403390
J62 | PID control (PID control block selection) | 403391
J63 | Overload Stop (Detected value) | 403392
J64 | Overload Stop (Detection level) | 403393
J65 | Overload Stop (Function selection) | 403394
J66 | Overload Stop (Operation condition) | 403395
J67 | Overload Stop (Timer) | 403396
J68 | Braking signal (Brake release current) | 403397
J69 | Braking signal (Brake release frequency) | 403398
J70 | Braking signal (Brake release timer) | 403399
J71 | Braking signal (Brake apply frequency) | 403400
J72 | Braking signal (Brake apply timer) | 403401
J73 | Position control (Start time) | 403402
J74 | Position control (Start point : Upper column) | 403403
J75 | Position control (Start point : Lower column) | 403404
J76 | Position control (Zero point : Upper column) | 403405
J77 | Position control (Zero point : Lower column) | 403406
J78 | Position control (Distance of low speed control : Upper column) | 403407
J79 | Position control (Distance of low speed control : Lower column) | 403408
J80 | Position control (Speed command on low speed control) | 403409
J81 | Position control (Objective Stop point : Upper column) | 403410
J82 | Position control (Objective Stop point : Lower column) | 403411
J83 | Position control (Permissible range of objective stop point) | 403412
J84 | Position control (End time) | 403413
J85 | Position control (Compensation of over travel) | 403414
J86 | Position control (Selection mode) | 403415
J87 | Position control (Compensation of over travel) | 403416
J88 | Position control (Selection mode) | 403417
J95 | Brake Signal (Release torque) | 403424
J96 | Brake Signal (Speed selection) | 403425
J97 | Brake Signal Servo lock (Gain) | 403426
J98 | Brake Signal (Completion timer) | 403427
J99 | Brake Signal (Completion range) | 403428
J105 | PID control (Display unit) | 403434
J106 | PID control (Maximum scale) | 403435
J107 | PID control (Minimum scale) | 403436
J136 | PID control (Multistep command 1) | 403465
J137 | PID control (Multistep command 2) | 403466
J138 | PID control (Multistep command 3) | 403467

## d
FUNCTION CODE | Detail | Address
d01 | Speed control 1 (Speed command filter) | 404866
d02 | Speed control 1 (Speed detection filter) | 404867
d03 | Speed control 1 P (Gain) | 404868
d04 | Speed control I (Integral time) | 404869
d05 | Speed control (FF gain) | 404870
d07 | Speed control (Notch filter resonance frequency) | 404872
d08 | Speed control (Notch filter attenuation level) | 404873
d09 | Speed control (JOG) (Speed command filter) | 404874
d10 | Speed control (Speed detection filter) | 404875
d11 | Speed control P (Gain) | 404876
d12 | Speed control I (Integral time) | 404877
d14 | Speed control Feedback (Feedback input) (Pulse input format) | 404879
d15 | Speed control (Encoder pulse count) | 404880
d16 | Speed control (Pulse scaling factor 1) | 404881
d17 | Speed control (Pulse scaling factor 2) | 404882
d21 | Speed agreement / PG error (Detection width) | 404886
d22 | Speed agreement / PG error (Detection timer) | 404887
d23 | PG error processing | 404888
d24 | Zero speed control | 404889
d25 | ASR switching time | 404890
d32 | Torque control (Speed limiting 1) | 404897
d33 | Torque control (Speed limiting 2) | 404898
d35 | Over speed detection level | 404900
d41 | Application control selection | 404906
d51 | Application control selection (For manufacturer) | 404916
d52 | Application control selection (For manufacturer) | 404917
d55 | Application control selection (For manufacturer) | 404918
d59 | Command (Pulse train input) (Pulse input format) | 404924
d60 | Command (Encoder pulse count) | 404925
d61 | Command (Filter time constant) | 404926
d62 | Command (Pulse scaling factor 1) | 404927
d63 | Command (Pulse scaling factor 2) | 404928
d67 | Starting characteristic | 404932
d69 | Starting characteristic (For manufacturer) | 404934
d70 | Speed control limiter | 404935
d71 | Master-follower operation (Main speed regulator gain) | 404936
d72 | Master-follower operation (APR P gain) | 404937
d73 | Master-follower operation (APR output +side limiter) | 404938
d74 | Master-follower operation (APR output -side limiter) | 404939
d75 | Master-follower operation (Z phase alignment gain) | 404940
d76 | Master-follower operation (Offset angle between master and follower) | 404941
d77 | Master-follower operation (Synchronous completion detection angle) | 404942
d78 | Master-follower operation (Excessive error detection level) | 404943
d79 | Master-follower operation (For manufacturer) | 404944
d88 | Master-follower operation (For manufacturer) | 404953
d90 | Magnetic flux level during deceleration under vector control for IM | 404955
d91 | (For manufacturer) | 404956
d92 | (For manufacturer) | 404957
d93 | (For manufacturer) | 404958
d94 | (For manufacturer) | 404959
d95 | (For manufacturer) | 404960
d96 | (For manufacturer) | 404961
d97 | (For manufacturer) | 404962
d99 | Extension function 1 | 404964

## u
FUNCTION CODE | Detail | Address
U00 | Customizable logic (Mode selection) | 402817
U01 | Customizable logic: Step 1 (Logic circuit) | 402818
U02 | Customizable logic: Step 1 (Input 1) | 402819
U03 | Customizable logic: Step 1 (Input 2) | 402820
U04 | Customizable logic: Step 1 (Function 1) | 402821
U05 | Customizable logic: Step 1 (Function 2) | 402822
U06 | Customizable logic: Step 2 (Logic circuit) | 402823
U07 | Customizable logic: Step 2 (Input 1) | 402824
U08 | Customizable logic: Step 2 (Input 2) | 402825
U09 | Customizable logic: Step 2 (Function 1) | 402826
U10 | Customizable logic: Step 2 (Function 2) | 402827
U11 | Customizable logic: Step 3 (Logic circuit) | 402828
U12 | Customizable logic: Step 3 (Input 1) | 402829
U13 | Customizable logic: Step 3 (Input 2) | 402830
U14 | Customizable logic: Step 3 (Function 1) | 402831
U15 | Customizable logic: Step 3 (Function 2) | 402832
U16 | Customizable logic: Step 4 (Logic circuit) | 402833
U17 | Customizable logic: Step 4 (Input 1) | 402834
U18 | Customizable logic: Step 4 (Input 2) | 402835
U19 | Customizable logic: Step 4 (Function 1) | 402836
U20 | Customizable logic: Step 4 (Function 2) | 402837
U21 | Customizable logic: Step 5 (Logic circuit) | 402838
U22 | Customizable logic: Step 5 (Input 1) | 402839
U23 | Customizable logic: Step 5 (Input 2) | 402840
U24 | Customizable logic: Step 5 (Function 1) | 402841
U25 | Customizable logic: Step 5 (Function 2) | 402842
U26 | Customizable logic: Step 6 (Logic circuit) | 402843
U27 | Customizable logic: Step 6 (Input 1) | 402844
U28 | Customizable logic: Step 6 (Input 2) | 402845
U29 | Customizable logic: Step 6 (Function 1) | 402846
U30 | Customizable logic: Step 6 (Function 2) | 402847
U31 | Customizable logic: Step 7 (Logic circuit) | 402848
U32 | Customizable logic: Step 7 (Input 1) | 402849
U33 | Customizable logic: Step 7 (Input 2) | 402850
U34 | Customizable logic: Step 7 (Function 1) | 402851
U35 | Customizable logic: Step 7 (Function 2) | 402852
U36 | Customizable logic: Step 8 (Logic circuit) | 402853
U37 | Customizable logic: Step 8 (Input 1) | 402854
U38 | Customizable logic: Step 8 (Input 2) | 402855
U39 | Customizable logic: Step 8 (Function 1) | 402856
U40 | Customizable logic: Step 8 (Function 2) | 402857
U41 | Customizable logic: Step 9 (Logic circuit) | 402858
U42 | Customizable logic: Step 9 (Input 1) | 402859
U43 | Customizable logic: Step 9 (Input 2) | 402860
U44 | Customizable logic: Step 9 (Function 1) | 402861
U45 | Customizable logic: Step 9 (Function 2) | 402862
U46 | Customizable logic: Step 10 (Logic circuit) | 402863
U47 | Customizable logic: Step 10 (Input 1) | 402864
U48 | Customizable logic: Step 10 (Input 2) | 402865
U49 | Customizable logic: Step 10 (Function 1) | 402866
U50 | Customizable logic: Step 10 (Function 2) | 402867
U51 | Customizable logic: Step 11 (Logic circuit) | 402868
U52 | Customizable logic: Step 11 (Input 1) | 402869
U53 | Customizable logic: Step 11 (Input 2) | 402870
U54 | Customizable logic: Step 11 (Function 1) | 402871
U55 | Customizable logic: Step 11 (Function 2) | 402872
U56 | Customizable logic: Step 12 (Logic circuit) | 402873
U57 | Customizable logic: Step 12 (Input 1) | 402874
U58 | Customizable logic: Step 12 (Input 2) | 402875
U59 | Customizable logic: Step 12 (Function 1) | 402876
U60 | Customizable logic: Step 12 (Function 2) | 402877
U61 | Customizable logic: Step 13 (Logic circuit) | 402878
U62 | Customizable logic: Step 13 (Input 1) | 402879
U63 | Customizable logic: Step 13 (Input 2) | 402880
U64 | Customizable logic: Step 13 (Function 1) | 402881
U65 | Customizable logic: Step 13 (Function 2) | 402882
U66 | Customizable logic: Step 14 (Logic circuit) | 402883
U67 | Customizable logic: Step 14 (Input 1) | 402884
U68 | Customizable logic: Step 14 (Input 2) | 402885
U69 | Customizable logic: Step 14 (Function 1) | 402886
U70 | Customizable logic: Step 14 (Function 2) | 402887
U71 | Customizable logic output signal 1 (Output selection) | 402888
U72 | Customizable logic output signal 2 | 402889
U73 | Customizable logic output signal 3 | 402890
U74 | Customizable logic output signal 4 | 402891
U75 | Customizable logic output signal 5 | 402892
U76 | Customizable logic output signal 6 | 402893
U77 | Customizable logic output signal 7 | 402894
U78 | Customizable logic output signal 8 | 402895
U79 | Customizable logic output signal 9 | 402896
U80 | Customizable logic output signal 10 | 402897
U81 | Customizable logic output signal 1 (Function selection) | 402898
U82 | Customizable logic output signal 2 | 402899
U83 | Customizable logic output signal 3 | 402900
U84 | Customizable logic output signal 4 | 402901
U85 | Customizable logic output signal 5 | 402902
U86 | Customizable logic output signal 6 | 402903
U87 | Customizable logic output signal 7 | 402904
U88 | Customizable logic output signal 8 | 402905
U89 | Customizable logic output signal 9 | 402906
U90 | Customizable logic output signal 10 | 402907
U91 | Customizable logic timer monitor (Step selection) | 402908
U92 | Customizable logic operation coefficient (Mantissa of KA1) | 402909
U93 | Customizable logic operation coefficient (Exponent part of KA1) | 402910
U94 | Customizable logic operation coefficient (Mantissa of KB1) | 402911
U95 | Customizable logic operation coefficient (Exponent part of KB1) | 402912
U96 | Customizable logic operation coefficient (Mantissa of KC1) | 402913
U97 | Customizable logic operation coefficient (Exponent part of KC1) | 402914
U100 | Task process end setting | 402917
U101 | Customizable logic Conversion operating point (X1) | 402918
U102 | Conversion operating point (Y1) | 402919
U103 | Conversion operating point (X2) | 402920
U104 | Conversion operating point (Y2) | 402921
U105 | Conversion operating point (X3) | 402922
U106 | Conversion operating point (Y3) | 402923
U107 | Customizable logic (Auto calculation of coefficients of approximate formula) | 402924
U121 | Customizable logic (User parameter 1) | 402938
U122 | Customizable logic (User parameter 2) | 402939
U123 | Customizable logic (User parameter 3) | 402940
U124 | Customizable logic (User parameter 4) | 402941
U125 | Customizable logic (User parameter 5) | 402942
U126 | Customizable logic (User parameter 6) | 402943
U127 | Customizable logic (User parameter 7) | 402944
U128 | Customizable logic (User parameter 8) | 402945
U129 | Customizable logic (User parameter 9) | 402946
U130 | Customizable logic (User parameter 10) | 402947
U131 | Customizable logic (User parameter 11) | 402948
U132 | Customizable logic (User parameter 12) | 402949
U133 | Customizable logic (User parameter 13) | 402950
U134 | Customizable logic (User parameter 14) | 402951
U135 | Customizable logic (User parameter 15) | 402952
U136 | Customizable logic (User parameter 16) | 402953
U137 | Customizable logic (User parameter 17) | 402954
U138 | Customizable logic (User parameter 18) | 402955
U139 | Customizable logic (User parameter 19) | 402956
U140 | Customizable logic (User parameter 20) | 402957
U171 | Customizable logic (Storage area 1) | 402988
U172 | Customizable logic: Step 13 (Storage area 2) | 402989
U173 | Customizable logic: Step 13 (Storage area 3) | 402990
U174 | Customizable logic: Step 13 (Storage area 4) | 402991
U175 | Customizable logic: Step 13 (Storage area 5) | 402992
U190 | Customizable logic step setting (Step number) | 403007
U191 | Customizable logic step setting (Circuit selection) | 403008
U192 | Customizable logic step setting (Input 1) | 403009
U193 | Customizable logic step setting (Input 2) | 403010
U194 | Customizable logic step setting (Function 1) | 403011
U195 | Customizable logic step setting (Function 2) | 403012
U196 | Customizable logic ROM version first 4 digits (Monitor) | 403013
U197 | Customizable logic ROM version first 4 digits (For user) | 403014
U198 | Customizable logic ROM version last 4 digits (Monitor) | 403015
U199 | Customizable logic ROM version last 4 digits (For user) | 403016

## y
FUNCTION CODE | Detail | Address
y01 | RS-485 communication 1 (Station address) | 403586
y02 | RS-485 communication 1 (Communications error processing) | 403587
y03 | RS-485 communication 1 (Timer) | 403588
y04 | RS-485 communication 1 (Baud rate) | 403589
y05 | RS-485 communication 1 (Data length) | 403590
y06 | RS-485 communication 1 (Parity check) | 403591
y07 | RS-485 communication 1 (Stop bits) | 403592
y08 | RS-485 communication 1 (No response error detection time) | 403593
y09 | RS-485 communication 1 (Response interval) | 403594
y10 | RS-485 communication 1 (Protocol selection) | 403595
y11 | RS-485 communication 2 (Station address) | 403596
y12 | RS-485 communication 2 (Communications error processing) | 403597
y13 | RS-485 communication 2 (Timer) | 403598
y14 | RS-485 communication 2 (Baud rate) | 403599
y15 | RS-485 communication 2 (Data length) | 403600
y16 | RS-485 communication 2 (Parity check) | 403601
y17 | RS-485 communication 2 (Stop bits) | 403602
y18 | RS-485 communication 2 (No response error detection time) | 403603
y19 | RS-485 communication 2 (Response interval) | 403604
y20 | RS-485 communication 2 (Protocol selection) | 403605
y21 | (For manufacturer) | 403606
y24 | (For manufacturer) | 403609
y25 | (For manufacturer) | 403610
y26 | (For manufacturer) | 403611
y27 | (For manufacturer) | 403612
y28 | (For manufacturer) | 403613
y29 | (For manufacturer) | 403614
y30 | (For manufacturer) | 403615
y31 | (For manufacturer) | 403616
y32 | (For manufacturer) | 403617
y33 | (For manufacturer) | 403618
y34 | (For manufacturer) | 403619
y35 | (For manufacturer) | 403620
y36 | (For manufacturer) | 403621
y95 | Data clear processing for communication error | 403680
y96 | For manufacturer | 403681
y97 | Communications Data Saving Method Selection | 403682
y98 | Bus Link Function (Mode selection) | 403683
y99 | Loader Link Function (Mode selection) | 403684

## o
FUNCTION CODE | Detail | Address
o01 | Terminal [O1] (Function selection) | 401538
o02 | Terminal [O2] (Function selection) | 401539
o03 | Terminal [O3] (Function selection) | 401540
o04 | Terminal [O4] (Function selection) | 401541
o05 | Terminal [O5] (Function selection) | 401542
o06 | Terminal [O6] (Function selection) | 401543
o07 | Terminal [O7] (Function selection) | 401544
o08 | Terminal [O8] (Function selection) | 401545
o19 | DI option (DI polarity selection) | 401556
o20 | DI option (DI mode selection) | 401557
o21 | DO option (DO mode selection) | 401558
o27 | Transmission error (Operation selection) | 401564
o28 | Transmission error (Timer time) | 401565
o30 | Bus setting parameter 01 | 401567
o31 | Bus setting parameter 02 | 401568
o32 | Bus setting parameter 03 | 401569
o33 | Bus setting parameter 04 | 401570
o34 | Bus setting parameter 05 | 401571
o35 | Bus setting parameter 06 | 401572
o36 | Bus setting parameter 07 | 401573
o37 | Bus setting parameter 08 | 401574
o38 | Bus setting parameter 09 | 401575
o39 | Bus setting parameter 10 | 401576
o40 | Write function code assignment 1 | 401577
o41 | Write function code assignment 2 | 401578
o42 | Write function code assignment 3 | 401579
o43 | Write function code assignment 4 | 401580
o44 | Write function code assignment 5 | 401581
o45 | Write function code assignment 6 | 401582
o46 | Write function code assignment 7 | 401583
o47 | Write function code assignment 8 | 401584
o48 | Read function code assignment 1 | 401585
o49 | Write function code assignment 2 | 401586
o50 | Write function code assignment 3 | 401587
o51 | Write function code assignment 4 | 401588
o52 | Write function code assignment 5 | 401589
o53 | Write function code assignment 6 | 401590
o54 | Write function code assignment 7 | 401591
o55 | Write function code assignment 8 | 401592
o56 | Write function code assignment 9 | 401593
o57 | Write function code assignment 10 | 401594
o58 | Write function code assignment 11 | 401595
o59 | Write function code assignment 12 | 401596
o60 | Terminal [32] (Function selection) | 401597
o61 | Terminal [32] (Offset adjustment) | 401598
o62 | Terminal [32] (Gain adjustment) | 401599
o63 | Terminal [32] (Filter setting) | 401600
o64 | Terminal [32] (Gain reference point) | 401601
o65 | Terminal [32] (Polarity selection) | 401602
o66 | Terminal [32] (Bias) | 401603
o67 | Terminal [32](Bias reference point) | 401604
o69 | Terminal [32](Display unit) | 401606
o70 | Terminal [32](Maximum scale) | 401607
o71 | Terminal [32](Minimum scale) | 401608
o75 | Terminal [C2] (Range selection) | 401612
o76 | Terminal [Ao/CS2] (Function selection) | 401613
o77 | Terminal [Ao/CS2] (Offset adjustment) | 401614
o78 | Terminal [Ao/CS2] (Gain adjustment) | 401615
o79 | Terminal [Ao/CS2] (Filter setting) | 401616
o81 | Terminal [Ao/CS2] (Gain reference point) | 401618
o82 | Terminal [Ao/CS2] (Bias) | 401619
o83 | Terminal [Ao/CS2] (Bias reference point) | 401620
o85 | Terminal [Ao/CS2] (Display unit) | 401622
o86 | Terminal [Ao/CS2] (Maximum scale) | 401623
o87 | Terminal [Ao/CS2] (Minimum scale) | 401624
o90 | Terminal [Ao/CS2] (Function selection) | 401627
o91 | Terminal [Ao/CS2] (Output gain) | 401628
o93 | Terminal [Ao/CS2] (Polarity selection) | 401630
o96 | Terminal [CS/CS1] (Function selection) | 401633
o97 | Terminal [CS/CS1] (Output gain) | 401634
o101 | Terminal [I1] (Function selection) | 401638
o102 | Terminal [I2] (Function selection) | 401639
o103 | Terminal [I3] (Function selection) | 401640
o104 | Terminal [I4] (Function selection) | 401641
o105 | Terminal [I5] (Function selection) | 401642
o106 | Terminal [I6] (Function selection) | 401643
o107 | Terminal [I7] (Function selection) | 401644
o108 | Terminal [I8] (Function selection) | 401645
o109 | Terminal [I9] (Function selection) | 401646
o110 | Terminal [I10] (Function selection) | 401647
o111 | Terminal [I11] (Function selection) | 401648
o112 | Terminal [I12] (Function selection) | 401649
o113 | Terminal [I13] (Function selection) | 401650

## K
FUNCTION CODE | Detail | Address
K01 | Multifunction keypad TP-A1-E2C(Language selection) | 407170
K02 | Multifunction keypad(Backlight OFF time) | 407171
K03 | Multifunction keypad(Backlight brightness adjustment) | 407172
K04 | Multifunction keypad(Contrast adjustment) | 407173
K08 | Multifunction keypad(LCD monitor status display) | 407177
K15 | Multifunction keypad(Sub-monitor display selection) | 407184
K16 | Multifunction keypad(Sub-monitor 1 display selection) | 407185
K17 | Multifunction keypad(Sub-monitor 2 display selection) | 407186
K20 | Multifunction keypad(Bar graph 1 display selection) | 407189
K21 | Multifunction keypad(Bar graph 2 display selection) | 407190
K22 | Multifunction keypad(Bar graph 3 display selection) | 407191
K91 | Multifunction keypad(< key shortcut selection) | 407260
K92 | Multifunction keypad(> key shortcut selection) | 407261

## s
FUNCTION CODE | Detail | Address
S01 | Frequency reference (p.u.) | 401794
S02 | Torque command | 401795
S03 | Torque current command | 401796
S05 | Frequency reference | 401798
S06 | Operation command | 401799
S07 | Universal DO | 401800
S08 | Acceleration time F07 | 401801
S09 | Deceleration time F08 | 401802
S10 | Torque limit value 1-1 | 401803
S11 | Torque limit value 1-2 | 401804
S12 | Universal AO | 401805
S13 | PID command | 401806
S14 | Alarm reset command | 401807
S19 | Speed command | 401812

## M
FUNCTION CODE | Detail | Address
M01 | Frequency reference (p.u.) | 402050
M02 | Torque command | 402051
M03 | Torque current command | 402052
M04 | Flux command | 402053
M05 | Frequency reference | 402054
M06 | Output frequency 1 (p.u.) | 402055
M07 | Torque real value | 402056
M08 | Torque current | 402057
M09 | Output frequency | 402058
M10 | Input power | 402059
M11 | Output current effective value | 402060
M12 | Output voltage effective value | 402061
M13 | Operation command | 402062
M14 | Operation status | 402063
M15 | General-purpose output terminal information | 402064
M16 | Latest alarm contents | 402065
M17 | Last alarm contents | 402066
M18 | Second last alarm contents | 402067
M19 | Third last alarm contents | 402068
M20 | Cumulative operation time | 402069
M21 | DC link circuit voltage | 402070
M23 | Model code | 402072
M24 | Capacity code | 402073
M25 | ROM version | 402074
M26 | Transmission error transaction code | 402075
M27 | Frequency reference on alarm (p.u.) | 402076
M28 | Torque command on alarm | 402077
M29 | Torque current command on alarm | 402078
M30 | Flux command on alarm | 402079
M31 | Frequency reference on alarm | 402080
M32 | Output frequency 1 on alarm (p.u.) | 402081
M33 | Torque real value on alarm | 402082
M34 | Torque current on alarm | 402083
M35 | Output frequency on alarm | 402084
M36 | Input power on alarm | 402085
M37 | Output current effective value on alarm | 402086
M38 | Output voltage effective value on alarm | 402087
M39 | Operation command on alarm | 402088
M40 | Operation status on alarm | 402089
M41 | Output terminal information on alarm | 402090
M42 | Cumulative operation time on alarm | 402091
M43 | DC link circuit voltage on alarm | 402092
M44 | Inverter internal air temperature on alarm | 402093
M45 | Heat sink temperature on alarm | 402094
M46 | Life of main circuit capacitor | 402095
M47 | Life of PC board electrolytic capacitor | 402096
M48 | Life of heat sink | 402097
M49 | Input terminal voltage [12] | 402098
M50 | Input terminal current [C1] | 402099
M52 | Input terminal voltage [32] | 402101
M53 | Input terminal current [C2] | 402102
M54 | Input terminal voltage [V2] | 402103
M61 | Inverter internal air temperature | 402110
M62 | Heat sink temperature | 402111
M63 | Load factor | 402112
M64 | Motor output | 402113
M65 | Motor output on alarm | 402114
M66 | Speed detection | 402115
M67 | Transmission error processing code | 402116
M68 | PID final command | 402117
M69 | Inverter rated current | 402118
M70 | Operation status 2 | 402119
M71 | Input terminal information | 402120
M72 | PID feedback value | 402121
M73 | PID output | 402122
M74 | Operating status 2 | 402123
M76 | Main circuit capacitor life (elapsed time) | 402125
M77 | Main circuit capacitor life (remaining time) | 402126
M78 | Rotation speed command | 402127
M79 | Rotation speed | 402128
M81 | Remaining time before maintenance (M1) | 402130
M85 | No. of starting times before maintenance (M1) | 402134
M86 | Light alarm (latest) | 402135
M87 | Light alarm (last) | 402136
M88 | Light alarm (second last) | 402137
M89 | Light alarm (third last) | 402138

## W
FUNCTION CODE | Detail | Address
W01 | Operation status | 403842
W02 | Frequency reference | 403843
W03 | Output frequency (before slip compensation) | 403844
W04 | Output frequency (after slip compensation) | 403845
W05 | Output current | 403846
W06 | Output voltage | 403847
W07 | Torque | 403848
W08 | Rotation speed | 403849
W09 | Load rotation speed | 403850
W10 | Line speed | 403851
W11 | PID process command | 403852
W12 | PID feedback value | 403853
W13 | Level of torque value A | 403854
W14 | Level of torque value B | 403855
W15 | Ratio value | 403856
W16 | Rotation speed set value | 403857
W17 | Load speed set value | 403858
W18 | Line speed set value | 403859
W19 | Constant feed time set value | 403860
W20 | Constant feed time | 403861
W21 | Input power | 403862
W22 | Motor output | 403863
W23 | Load rate | 403864
W24 | Torque current | 403865
W26 | Flux reference | 403867
W27 | Timer operation remaining time | 403868
W28 | Operation command source | 403869
W29 | Frequency and PID command source | 403870
W30 | Speed at percentage | 403871
W31 | Speed set value at percentage | 403872
W32 | PID output | 403873
W33 | Analog input monitor | 403874
W35 | Terminal [32] input voltage | 403876
W36 | Terminal [C2] input current | 403877
W37 | Terminal [A0] output voltage | 403878
W38 | Terminal [CS] output frequency | 403879
W39 | Pulse input monitor [X7] | 403880
W40 | Control circuit terminal (input) | 403881
W41 | Control circuit terminal (output) | 403882
W42 | Communications control signal (input) | 403883
W43 | Communications control signal (output) | 403884
W44 | Terminal [12] input voltage | 403885
W45 | Terminal [C1] input current | 403886
W46 | FMA output voltage | 403887
W47 | FMP output voltage | 403888
W48 | FMP output frequency | 403889
W49 | V2 terminal input voltage | 403890
W50 | FMA output current | 403891
W51 | Situation of input terminals on DIO option | 403892
W52 | Situation of output terminals on DIO option | 403893
W53 | Pulse input (Master - side A/B phase) | 403894
W54 | Pulse input (Master - side Z phase) | 403895
W55 | Pulse input (Slave - side A/B phase) | 403896
W56 | Pulse input (Slave - side Z phase) | 403897
W57 | Current Position Pulse (Upper column) | 403898
W58 | Current Position Pulse (Lower column) | 403899
W59 | Stop Position Pulse (Upper column) | 403900
W60 | Stop Position Pulse (Lower column) | 403901
W61 | Difference Pulse of Position (Upper column) | 403902
W62 | Difference Pulse of Position (Lower column) | 403903
W63 | Positioning Status | 403904
W66 | Deviation for SY synchronization | 403907
W67 | Cumulative operation time of electrolytic | 403908
W68 | Cumulative operation time of cooling fan | 403909
W70 | Cumulative operation time | 403911
W71 | DC link circuit voltage | 403912
W72 | Internal air highest temperature | 403913
W73 | Heat sink maximum temperature | 403914
W74 | Maximum effective current value | 403915
W75 | Main circuit capacitor's capacitor | 403916
W76 | Cumulative ope. time of capacitor on PC board | 403917
W77 | Cumulative ope. time of cooling fan | 403918
W78 | Number of startups | 403919
W81 | Integrating electric power | 403922
W82 | Data used integrating electric power | 403923
W83 | Number of RS485 ch1 errors | 403924
W84 | Contents of RS485 ch1 error | 403925
W85 | Number of RS485 ch2 errors | 403926
W87 | Inverter's keypad's ROM version (CPU1) | 403928
W88 | Inverter's keypad's ROM version (CPU2) | 403929
W89 | Remote keypad's ROM version | 403930
W90 | Option 1 ROM version | 403931
W94 | Contents of RS485 ch2 error | 403935
W95 | Number of option communications errors | 403936
W96 | Option communicate error contents | 403937

## X
FUNCTION CODE | Detail | Address
X00 | Alarm history (latest) | 404097
X01 | Multiple alarm 1 (latest) | 404098
X02 | Multiple alarm 2 (latest) | 404099
X03 | Sub code (latest) | 404100
X04 | Multiple alarm subcode (Latest, second) | 404101
X05 | Alarm history (last) | 404102
X06 | Multiple alarm 1 (last) | 404103
X07 | Multiple alarm 2 (last) | 404104
X08 | Sub code (last) | 404105
X09 | Multiple alarm subcode (Last, second) | 404106
X10 | Alarm history (second last) | 404107
X11 | Multiple alarm 1 (second last) | 404108
X12 | Multiple alarm 2 (second last) | 404109
X13 | Sub code (second last) | 404110
X14 | Multiple alarm subcode (Second last, second) | 404111
X15 | Alarm history (third last) | 404112
X16 | Multiple alarm 1 (third last) | 404113
X17 | Multiple alarm 2 (third last) | 404114
X18 | Sub code (last) | 404115
X19 | Multiple alarm subcode (Third last, second) | 404116
X20 | Latest info. on alarm (output frequency) | 404117
X21 | Latest info. on alarm (output current) | 404118
X22 | Latest info. on alarm (output voltage) | 404119
X23 | Latest info. on alarm (Torque) | 404120
X24 | Latest info. on alarm (set frequency) | 404121
X25 | Latest info. on alarm (operation status) | 404122
X26 | Latest info. on alarm (cumulative ope. time) | 404123
X27 | Latest info. on alarm (number of startups) | 404124
X28 | Latest info. on alarm (DC link circuit voltage) | 404125
X29 | Latest info. on alarm (internal air temperature) | 404126
X30 | Latest info. on alarm (heat sink temperature) | 404127
X31 | Latest info. on alarm (input terminal) | 404128
X32 | Latest info. on alarm (output terminal) | 404129
X33 | Latest info. on alarm (input terminal(com.)) | 404130
X34 | Latest info. on alarm (output terminal(com.)) | 404131
X35 | Latest info. on alarm (Power consumption during alarm) | 404132
X36 | Latest info. on alarm (Operation status 2) | 404133
X37 | Latest info. on alarm (Speed detection) | 404134
X38 | Latest info. on alarm (Operation status 3) | 404135
X60 | Last info. on alarm (output frequency) | 404157
X61 | Last info. on alarm (output current) | 404158
X62 | Last info. on alarm (output voltage) | 404159
X63 | Last info. on alarm (Torque) | 404160
X64 | Last info. on alarm (set frequency) | 404161
X65 | Last info. on alarm (operation status) | 404162
X66 | Last info. on alarm (cumulative ope. time) | 404163
X67 | Last info. on alarm (number of startups) | 404164
X68 | Last info. on alarm (DC link circuit voltage) | 404165
X69 | Last info. on alarm (internal air temperature) | 404166
X70 | Last info. on alarm (heat sink temperature) | 404167
X71 | Last info. on alarm (input terminal) | 404168
X72 | Last info. on alarm (output terminal) | 404169
X73 | Last info. on alarm (input terminal(com.)) | 404170
X74 | Last info. on alarm (output terminal(com.)) | 404171
X76 | Last info. on alarm (Operation status 2) | 404173
X77 | Last info. on alarm (Speed detection) | 404174
X78 | Last info. on alarm (Operation status 3) | 404175
X89 | Customizable logic (Digital I/O) | 404186
X90 | Customizable logic (Timer monitor) | 404187
X91 | Customizable logic (Analog input 1) | 404188
X92 | Customizable logic (Analog input 2) | 404189
X93 | Customizable logic (Analog output) | 404190
X94 | Relay output terminal information | 404191
X97 | Terminal (PTC) input voltage | 404194

## Z
FUNCTION CODE | Detail | Address
Z00 | Second last info. on alarm (output frequency) | 404353
Z01 | Second last info. on alarm (output current) | 404354
Z02 | Second last info. on alarm (output voltage) | 404355
Z03 | Second last info. on alarm (Torque) | 404356
Z04 | Second last info. on alarm (set frequency) | 404357
Z05 | Second last info. on alarm (operation status) | 404358
Z06 | Second last info. on alarm (cumulative ope. time) | 404359
Z07 | Second last info. on alarm (number of startups) | 404360
Z08 | Second last info. on alarm (DC link circuit voltage) | 404361
Z09 | Second last info. on alarm (internal air temperature) | 404362
Z10 | Second last info. on alarm (heat sink temperature) | 404363
Z11 | Second last info. on alarm (input terminal) | 404364
Z12 | Second last info. on alarm (output terminal) | 404365
Z13 | Second last info. on alarm (input terminal(com.)) | 404366
Z14 | Second last info. on alarm (output terminal(com.)) | 404367
Z16 | Second last info. on alarm (Operation status 2) | 404369
Z17 | Second last info. on alarm (Speed detection) | 404370
Z18 | Second last info. on alarm (Operation status 3) | 404371
Z40 | Cumulative operation time of motor (M1) | 404393
Z41 | Cumulative operation time of motor(M2) | 404394
Z44 | Number of starting time (M2) | 404397
Z48 | Retry history (Latest) | 404401
Z49 | Retry history (Last) | 404402
Z50 | Third last info. on alarm (output frequency) | 404403
Z51 | Third last info. on alarm (output current) | 404404
Z52 | Third last info. on alarm (output voltage) | 404405
Z53 | Third last info. on alarm (Torque) | 404406
Z54 | Third last info. on alarm (set frequency) | 404407
Z55 | Third last info. on alarm (operation status) | 404408
Z56 | Third last info. on alarm (cumulative ope. time) | 404409
Z57 | Third last info. on alarm (number of startups) | 404410
Z58 | Third last info. on alarm(DC link circuit voltage) | 404411
Z59 | Third last info. on alarm(internal air temperature) | 404412
Z60 | Third last info. on alarm(heat sink temperature) | 404413
Z61 | Third last info. on alarm(input terminal) | 404414
Z62 | Third last info. on alarm(output terminal) | 404415
Z63 | Third last info. on alarm(input terminal(com.)) | 404416
Z64 | Third last info. on alarm(output terminal(com.)) | 404417
Z66 | Third last info. on alarm(Operation status 2) | 404419
Z67 | Third last info. on alarm(Speed detection) | 404420
Z68 | Third last info. on alarm(Operation status 2) | 404421
Z78 | (For manufacturer) | 404431
Z79 | (For manufacturer) | 404432
Z80 | Speed detection | 404433
Z81 | Output torque | 404434
Z82 | Load factor | 404435
Z83 | Motor output | 404436
Z84 | Output current | 404437
Z85 | PID feedback value | 404438
Z86 | Power consumption | 404439
Z87 | PID output | 404440
Z88 | Integral power | 404441
Z90 | Current Position Pulse (Upper column) | 404443
Z91 | Current Position Pulse (Lower column) | 404444
Z92 | Stop Position Pulse (Upper column) | 404445
Z93 | Stop Position Pulse (Lower column) | 404446
Z94 | Difference Pulse of Position (Upper column) | 404447
Z95 | Difference Pulse of Position (Lower column) | 404448